## Stanby-Gen.
Utility Name:
Generator Summary
Generator Information
[11 empty] | Allowable Motor HP @ 480V (Soft-start) |  |  |  | Fuel Tank | Fuel
| Generator | PG&E | Main |  | Year |  |  | Max |  | Allowable Motor HP @ 480V (Across-the-line) |  |  |  |  | Capacity @ | Use @
| Towing | Rate | Breaker | Estimate | Unit |  | Unit | Capacity | [6 empty] | Max Load | Max Load
Station Stationary | License | Sched | (Amps) | Number | Installed | Manufacturer | Cost | (Kw) | KVA |  |  | Amps | Pole | Volts | (gallons) | (gal./hr.)
Station 1 |  | E20S | 4000 | G1-XXX | 2001 | Katolight |  | 1600 | 2000 |  |  | 2406 | 3 | 277/408 | 945 | 98
Station 2 |  | E20S | 2- 600 | G7-XXX | 2007 | Katolight |  | 175 | 218.8 |  |  | 607 | 3 | 120/208 | 315 | 13.6
Station 3 |  | E19S | 1000 | E7-XXX | 1997 | Katolight |  | 750 | 937.5 |  |  | 902 | 3 | 480 | 400 | 56
Station 4 |  | A1 | N/A |  |  | Katolight |  | 275 | 343 |  |  | 413 | 3 | 277/480 | N/A | N/A
Station 1
Station 1
Station 1
Station 1
Station 1
Station 1
Station 1
Station 1
Generator Information for Portable Generators
Station Portable
Location X | A |  |  | EX-XXX | 1993 | Katolight | 58238 | 275 | 343.75 | 125 | 250 | 413/827 | 3 | 120/240 240/480 | 250 | 21.2
Location X | A
Location X | C
Location X | A
Location X | C
Location X | C
Location X | A
Location X | A
Location X | C
Location X | C
Location X | C
Location X | C
Location X | C
Location X | C
Location X | C
Location X | C
Location X | C
Location X | C
Location X | C
Location X | C
Corrections made through audit
Information missing and needed

## PortGenReceptacles
Utility Name
Stations with Generator Receptacles for Portable Generators
|  |  |  | Motor Information | [5 empty] | Automatic Transfer Switch Information | [5 empty] | Portable Generator Storage Location, Number, Compatability (Compatible at Station = x)
|  |  | Selected | [12 empty] | Station 1 | Station 2 | Station 3 | Station 4 | Station 5 | Station 6 | Station 7 | Station 8 | Station 9 | Station 10 | Station 11 | Station 12 | Station 13 | Station 14 | Station 15 | Station 16 | Station 17 | Station 18 | Station 19 | Station 20
| PG&E | Main | Booster/ | [7 empty] | Year
| Rate | Breaker | Well | Motor |  |  |  |  | NEMA | Estimate | Unit |  |  |  |  | #10 | #11 | #41 | #42 | #43 | #44 | #53 | #54 | #58 | #59 | #60 | #61 | #62 | #63 | #64 | #65 | #66 | #67 | #68 | #69
Station | Sched. | (Amps) | Units | Mgf. | HP | Type | Volts | FLA | Code | Number | Installed | Mgf. | Amps | Pole | Volts
Location | A6P | 225 | B-1 | US(HE) | 75 | VHS | 460 | 87 | G | E5-### | 1995 | Generac | 400 | 3 | 480 | ALL | ALL | ALL | ONE | ONE | ONE | ALL | ALL | ONE | ONE | ONE | ONE | ONE | ONE | ONE | ONE | ONE | ONE | ONE | ONE
|  | 400 | B-2 | US | 125 | VHS | 460 | 145 | G | [9 empty] | ONE | ONE | NO |  |  | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO
Location | A1P | 200 | B-1 | US(HE) | 20 | VHS | 460 | 23.7 | G | E4-### | 1994 | Generac | 200 | 3 | 480 | ALL | ALL | ALL | ALL | ALL | ALL | ALL | ALL | ALL | ALL | ALL | ALL | ALL | ALL | ALL | ALL | ALL | ALL | ALL | ALL
|  |  | B-2 | US(HE) | 20 | VHS | 460 | 25.8 | G
Location | A6 | 200 | B-1 | Pleuger | 75 | SUB | 460 | 104 |  | G7-### | 2011 | Generac | 200 | 3 | 480 | NO | NO | NO | ONE | ONE | ONE | NO | NO | ONE | ONE | ONE | ONE | ONE | ONE | ONE | ONE | ONE | ONE | ONE | ONE
Location | A1 | 200 | B-1 | BJ | 40 | SUB | 460 | 50 | G | E9-### | 1999 | Generac | 300 | 3 | 480 | NO | NO | NO | ONE | ONE | ONE | NO | NO | ONE | ONE | ONE | ONE | ONE | ONE | ONE | ONE | ONE | ONE | ONE | ONE
Location | A10S | 1000 | B-1 | GE (HE) | 125 | Horiz. | 460 | 142 | G | G4-### | 2004 | Generac | 1000 | 3 | 480 | #10: 1B, 1W
|  |  | B-2 | GE (HE) | 125 | Horiz. | 460 | 143 | G | [6 empty] | #10: 1B, 1W
|  |  | B-4 | GE | 150 | VHS | 460 | 165 | [7 empty] | #10: 1B, 1W
|  |  | W-6 | GE | 125 | VHS | 460 | 137 | G | [6 empty] | #10: 1B, 1W
|  |  | W-7 | GE (HE) | 125 | VHS | 460 | 141 | G | [6 empty] | #10: 1B, 1W
Location | A10 | 800 | B-1 | US | 100 | Horiz. | 440 | 167 |  | E5-### | 1995 | Generac | 800 | 3 | 480 | 1&2 | 1&2 | 1&2 | ONE | ONE | ONE | 1&2 | 1&2 | ONE | ONE | ONE | ONE | ONE | ONE | ONE | ONE | ONE | ONE | ONE | ONE
|  |  | B-2 | Pleuger | 150 | SUB | 440 | 133 | [7 empty] | 1&2 | 1&2 | 1&2 | NO | NO | NO | 1&2 | 1&2 | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO
|  |  | B-3 | US | 200 | VHS | 440 | 228 | G | [6 empty] | ONE | ONE | ONE | NO | NO | NO | ONE | ONE | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO
Corrections made through audit
Information missing and needed